## Tabelle1
type 412-36mm-4kN
OZ | PosArt | Kurztext | Langtext | Menge | Einheit | EP
Preliminary note
Technical conditions for the raised floor system as described in the specification sheet below:
The offered service includes the creation of a raise floor facility with installation space for offices and administrative buildings.
The structural parts (such as pillars, walls) to which the raised floor must be connected consist of reinforced concrete or simple masonry. Until the installation of the raised floor, the following works are carried out on site: - Window and door frame installation, as well as installation of ceiling cover - Installations for heating, ventilation, plumbing and electrical systems
After the rooms have been cleared by the construction management, the installation of the raised floor can start immediately. The designated areas are swept clean.
Performance (without hourly wage work):
|  | approach and preparation | Construction site approach, site preparation |  | pcs. | 0
|  | check soil and prepare | vacuum clean-swept raw soil and prepare for sealing; Visual inspection of the floor for porosity, cracks, adhesion and compliance with applicable tolerances etc. |  | m² | 0
|  | compensation | Compensation of raw soil tolerances |  | m² | 0
|  | surcharge difficult assembly | Surcharge for difficult installation in areas with tolerances outside DIN 18 202, evenness Table 3, line 2 and angle deviations Table 2, line 1, including the provision of pedestals at different heights |  | m² | 0
|  | sealing dispersion | Raw floor sealed with Weiss sealing dispersion, 1-component synthetic resin dispersion, solvent-free and low-emission, matched to the pedestal glue |  | m² | 0
|  | surcharge | Surcharge for execution in 2-component epoxy resin system |  | m² | 0
|  | surcharge | Surcharge for sealing the walls up to raised floor height for ventilation in the floor |  | m² | 0
|  | measuring the raised floor grid | Measuring the raised floor grid before carrying out the installation work. Permanent marking with paint spray or paint chalk line on the untreated floor in a grid of 3 x 3 m. Inclusive separate arrival of the assembly staff. |  | m² | 0
Weiss Doppelbodensystem type 412-36mm-4kN
|  | deliver and assemble | Supply and installation of a raised floor system with certificate of conformity according to DIN EN 12 825 and application guideline to DIN EN 12 825. For the system the certificate of conformity of a recognized certifier has to be presented.
|  | classification | Classification according to DIN EN 12 825 and application policy: Load level: 4,000 N Point load: 4,000 N Breaking load:> = 8,000 N Element class: 3 Grid 600 x 600 mm Panel thickness: 36.5 mm plus cover thickness
|  | building material and fire resistance class | Building material class according to DIN EN 13 501-1: A1 Building material class according to DIN 4102: A2 Fire rating: F30 / REI30 possible Technical data according to product data sheets, certificates, test reports and test certificates.
|  | FFH | The construction height (FFH = finished floor height) of the raised floor is: ___________________ mm
The raised floor panel consists of a gypsum fiberboard at least 36 mm thick, which is frictionally connected on the underside to a galvanized sheet steel (0.4 mm). The plate edges are cut diagonally and covered with a plastic edge. All pedestals must be made of galvanized steel, free from chromium-VI, and be infinitely adjustable in height. For sound insulation and to ensure the electrical conductivity an electrically conductive cap has to be put on the pedestal head. Otherwise as stated in the preliminary remarks.
|  | type 412-36mm-4kN | fabricate of raised floor system: Weiss Doppelbodensystem 412-36mm-4kN or similar offered product: _______________________________ |  | m² | 0
cover
|  | cover | [Manufacturer + type flooring] [Type of cover, z. B. HPL] cover, factory glued to the raised floor panels. Product: [Manufacturer + type cover] Bleeder resistance in the system: ≤ xxx ohms Charging voltage: ≤ 2 kV (or xxx kV, if lower) Anti-slip: R9 (or R10 ....) Thickness: xxx mm Thickness: yyy mm (delete as appropriate) For technical data see product data sheet and declaration of performance of the cover manufacturer. |  | m² | 0
Each panel must rest freely, be easily removable and interchangeable.
Cut-outs for cables and climate control must be possible on every full raised floor panel in order to be able to variably select the machine layout.
For the bridging of heating pipes or other installations bridging beams for one or two dropped pedestals must be provided.
The connections to supporting pillars, walls and on-site facilities are dull and accordingly airtight and provided with a wall seal.
The dimensions required for installation shall be determined on the basis of the erection drawings to be made by the contractor on the basis of the design drawings of the design office and the local inspection. All assembly drawings of the contractor must be submitted to the planning office or site management for approval in quadruplicate. The contractor will receive a copy signed back after checking the documents.
The service offered includes the production of all construction parts and the delivery free point of use as well as the complete assembly in acceptance-ready, ready-to-use execution, according to the approved construction drawings and the specifications, including all fringe benefits and utilities.
Additional requirement and burden: In the course of further interior work, non-load-bearing partition walls are placed on the raised floor construction on site. The raised floor is secured by additional pedestals per meter of partition.
substructure
|  | substructure | The substructure must consist of individual, lockable and height-adjustable pedestals, which ensure a perfect leveling and beaded stringers type WEISS.
pedestals
|  | pedestals | height adjustable tubular steel pedestal for FFH ___ mm, type CS / DS, cross section depending on height for 4 kN, galvanized. |  | pcs. | 0
|  | bolt adhesive | Bolt adhesive for securing against automatic adjustment |  | pcs. | 0
|  | intermediate plates | PE/ABS intermediate plates conductive |  | pcs. | 0
|  | wall angle | Supply and install an angle for wall fixation as a replacement for a pedestal. Only possible on sufficiently load-bearing concrete walls. |  | pcs. | 0
|  | Weiss U-stringer | Horizontal stiffening of the substructure and increase of the nominal load with stringer, U-stringer 10x30x10x0,8x537 mm, (from 500 mm) |  | pcs. | 0
|  | surcharge | Surcharge for screwing the stringer (Weiss U- stringer), (from 900 mm) |  | pcs. | 0
|  | Weiss stringer | Horizontal stiffening of the substructure and increase of the nominal load with stringer, crimped and perforated, C-grid 30x30x30x1x537 mm |  | pcs. | 0
|  | surcharge | Surcharge for screwing the stringer (Weiss stringer beaded), (from 900 mm) |  | pcs. | 0
|  | Weiss tube-stringer | Horizontal stiffening of the substructure and increase of the nominal load with stringer, perforated, rectangular tube 30x30x1,8x537 mm. |  | pcs. | 0
|  | surcharge | Surcharge for screwing the stringer (Weiss tube-stringer), (from 900 mm) |  | pcs. | 0
|  | surcharge special size | Surcharge to item XXX for delivery and installation of special dimension panels. Gypsum fiberboard / chipboard with underside aluminium / steel sheet Dimension: 600 x 750 mm 600 x 800 mm _____ x 600 mm (350 to 600 possible) (delete as appropriate) |  | pcs. | 0
|  | screw connection | The screw connection of the raised floor panel consists of a stepped bore and a through hole, a covering disc to cover the screw is inserted into the uppermost level of the step milling, the panels are factory set in all 4 corners In the area of rising components, bridging, etc., all possible corners are screwed in place, no screwing takes place at corners or corners with pedestals in a different position. Securing against lifting possible. |  | m² | 0
|  | surcharge | Surcharge to pos. xxx, improvement of the impact sound properties by the installation of footfall sound insulation plates under the pedestals. |  | m² | 0
|  | expansion joint | Delivering and installing an expansion joint in the raised floor: Recording movements in the following axes: X: __________ mm Y: __________ mm Z: __________ mm (delete as appropriate)Pedestals in the area of the joint are to be pegged. From a pedestal height of 200 mm every second support has to be braced. Product: Migua type __________ or equivalent. offered product: _________________________ |  | rm | 0
|  | thermal insulation (fleece) | Supply and installation of a thermal insulation in the floor cavity. The thermal insulation is made of mineral wool, laminated on the upper side with fleece, WLG 035. Thickness: __________ mm |  | m² | 0
|  | thermal insulation | Supply and installation of a thermal insulation in the floor cavity. The thermal insulation is made of mineral wool, laminated on the upper side with aluminium, WLG 035. Thickness: __________ mm |  | m² | 0
|  | surcharge | Surcharge for fire retardant version in REI 30. A fire resistance test report shall be submitted to the system. |  | m² | 0
|  | surcharge | Surcharge to item xxx for fire-retardant version in F30 in necessary corridors. A general appraisal certificate for the system must be submitted. |  | m² | 0
|  | surcharge | Surcharge to item xxx for fire-retardant version in F30 in other areas, without necessary corridors. A general appraisal certificate for the system must be submitted. |  | m² | 0
|  | fire barrier F30 - gypsum | Delivering and mounting a F30 firewall. The gypsum stones used are connected to a system-specific adhesive. The transition to the raised floor is sealed with mineral wool. Height: __________ mm |  | rm | 0
|  | fire barrier F30 - aerated concrete | Delivering and mounting a F30 firewall. The used aerated concrete blocks are bonded to a system-specific adhesive. The transition to the raised floor is sealed with mineral wool. Height: __________ mm |  | rm | 0
|  | surcharge | Surcharge for difficult installation on uneven bare floor contrary to DIN EN 18202 including appropriate supports |  | m² | 0
|  | doweling metal knock-in dowels | Dowelling of the pedestals on the unfinished floor with metal impact anchors, 2-fold |  | m² | 0
|  | surcharge | Surcharge for 3- or 4-fold dowelling as pos. before |  | m² | 0
|  | dowelling plastic dowels | Dowelling of the pedestals on the screed with plastic dowel and screw, 2-fold |  | m² | 0
|  | surcharge | Surcharge for 3- or 4-fold dowelling as pos. before |  | m² | 0
|  | load distribution plates | Load distribution plates made of galvanized sheet steel, 200x200x3 mm, delivering and assembling. |  | m² | 0
|  | surcharge | Surcharge for execution of the load distribution panel made of porcelain stoneware, 200x200x10 mm. |  | m² | 0
|  | bridging support up to 900 mm | Bridges made of galvanized steel C-profiles for bridging areas where it is not possible to set up pedestals. The load-bearing capacity of the installed bridging system corresponds to that of the raised floor system. Support-width up to 900 mm |  | pcs. | 0
|  | bridging support up to 1200 mm | Bridges made of galvanized steel C-profiles for bridging areas where it is not possible to set up pedestals. The load-bearing capacity of the installed bridging system corresponds to that of the raised floor system. Support-width up to 1200 mm |  | pcs. | 0
|  | bridging support up to 1800 mm | Bridges made of galvanized steel C-profiles for bridging areas where it is not possible to set up pedestals. The load-bearing capacity of the installed bridging system corresponds to that of the raised floor system. Support-width up to 1800 mm |  | pcs. | 0
|  | surcharge | Surcharge for adjusting the floor panels to straight ascending components. The gates are sealed with emission-free dispersion. A cover band is inserted. |  | rm | 0
|  | surcharge | Allowance for adjusting the floor slabs to round / sloping ascending components. The gates are sealed with emission-free dispersion. A cover band is inserted. |  | rm | 0
|  | surcharge | Surcharge as before, but adapt to columns or pillars with necessary additional pedestals. |  | rm | 0
|  | surcharge | Surcharge for adjusting the floor to doors or wall niches. |  | rm | 0
|  | compriband | Delivery and installation of a permanently elastic compression belt as a wall seal Thickness x width 5 x 9 mm 5 x 15 mm 10 x 15 mm (delete as appropriate) |  | rm | 0
|  | vapor barrier | Barrier against rising damp according to DIN 18195-4. general appraisal certificate is available. The substrate must be suitable for receiving the seal. Delivery and professionally glued over the entire surface Installing aluminium composite foil with glass mesh fabric insert on self-adhesive elastomeric bitumen; all impacts min. 100 mm overlapping cold glued and pulled up at the edges. Thickness about 0.4 mm |  | m² | 0
|  | partition for air guidance | Delivering and mounting a single-shell foreclosure within the floor cavity for airflow purposes. The bulkhead is made of wood-based material, coated on both sides with melamine, 19 mm thick. All joints are sealed with sealing tape / sealant. Height: __________ mm |  | rm | 0
|  | partitioning for sound insulation | Supply and installation of a partition to reduce the transmission of airborne sound in the floor cavity, consisting of mineral wool with a width of 300 mm, compressed between unfinished floor and raised floor. Height: __________ mm |  | rm | 0
|  | surcharge | Surcharge for airtight packaging of mineral wool |  |  | 0
|  | surcharge | Surcharge for previous position, for airtight packaging of mineral wool in PE film, in air-bearing floors. |  | rm | 0
|  | front foreclosure | Delivery and installation of a front foreclosure, consisting of wood-based material, both sides coated with melamine, aluminium angles, anchoring of the edge supports and bracing. The front foreclosure serves as a vertical closure of a raised floor ending free in the room. Height: __________ mm |  | rm | 0
|  | surcharge | Surcharge for item xxx, extra charge for the version with floor covering same as the raised floor. Wooden plates due to the bonding possibly without melamine coating. Height: __________ mm |  | rm | 0
|  | surcharge | Surcharge for item xxx, extra charge for the execution of the partition made of gypsum fiber board, building material class A1 according to DIN EN 13 501. Height: __________ mm |  | rm | 0
|  | cut-outs | Cut-outs for heating pipes |  | pcs. | 0
|  | cut-outs | Surcharge for pos. xxx, factory / on-site production of a round cut-out up to - 110 mm - 210 mm - 310 mm - 410 mm (delete as appropriate) Depending on the geometry and position of the cut-outs, the load capacity of the raised floor panel can be reduced. If necessary, load-increasing measures are to be commissioned separately. |  | pcs. | 0
|  | surcharge | Extra charge for previous position, for producing a stepped rebate |  | pcs. | 0
|  | cut-outs | Surcharge for pos. xxx, factory / on-site production of a rectangular cut-out up to the circumference - 440 mm - 840 mm - 1240 mm - 1640 mm (delete as appropriate) The corners are rounded with radius up to 10 mm. Depending on the geometry and position of the cut-outs, the load capacity of the raised floor panel can be reduced. If necessary, load-increasing measures are to be commissioned separately. |  | pcs. | 0
|  | surcharge | Extra charge for Pos. Before, for producing a stepped rebate, z. B. for air outlets, swirl nozzles, vacuum cleaner connections For several rebate folds per cut, price per fold. |  | pcs. | 0
|  | surcharge | Extra charge for xxx, for production of the cut-out with corners without rounding (radius <= 1 mm) |  | pcs. | 0
|  | surcharge | Surcharge for Pos. xxx, for the production of the cut-out with corners without rounding, for panels coated with steel (radius <= 1 mm) |  | pcs. | 0
|  | surcharge | Extra charge for pos. xxx, for production of a precisely fitting cut-out with minimized joint, for inserts without a fold overlapping the cover. |  | pcs. | 0
|  | safety cover | Deliver and install a safety cover for cut-out Dimensions: __________ x __________ mm Execution in steel sheet / wooden material Disassembly and disposal on site (delete as appropriate) |  | pcs. | 0
|  | surcharge | surcharge to previous position, for disassembly and disposal of the protective cover |  | pcs. | 0
|  | brush insert for cable entry | Supply and installation of a brush insert for cable entry for raised floor panels. Installation dimension / inside dimension: - 370 x 290 mm / 316 x 200 mm - 270 x 290 mm / 216 x 200 mm - 170 x 290 mm / 117 x 200 mm (delete as appropriate) The insert made of aluminium and plastic has on two sides, facing, two-ply brush rows. These significantly reduce the leakage air flow, especially in ventilated floors, and result in a pleasant visual appearance of the grommet. The insert is screwed into a correspondingly large cut-out, a fold overlaps the floor covering. The necessary section is to be ordered separately. |  | pcs. | 0
|  | ventilation-twist outlet | Supply and installation of a twist outlet for ventilation, with a diameter of 150 mm, for an air flow rate per plate of __________ m³ / h at a differential pressure of __________ Pa. Colour grey Product: Krantz twist lid DN 150 The necessary section has to be ordered separately. |  | pcs. | 0
|  | surcharge | Surcharge for previous pos., for delivery and installation of a dirt collector Krantz KB 150 for the twist outlet. |  | pcs. | 0
|  | surcharge | Surcharge for pos. xxx, for supply and installation of a clamping ring for the twist outlet. |  | pcs. | 0
|  | stairs | Delivery and installation of a staircase at the transition from raw to raised floor. Stairs _______- tiered, made of wood-based material (each 150 mm step height, 300 mm step depth), _______ mm wide, with the same covering as the panels, with aluminium treads at the step edges, incl. mounting material For stem / installation (delete as appropriate). Price per meter width of the stairs. |  | rm | 0
|  | ramp | Delivering and installing a ramp for driving the raised floor from the unfinished floor. Existing loads, wheel spacing and accelerations must be indicated. Consisting of 38 mm thick, highly compacted wood-based panel, with aluminium chock wrench. For transport and assembly divided. SW-substructure, size : Height x length x width _______ x _______ x _______ mm |  | m² | 0
|  | handrail | Delivery and installation of a system railing, consisting of aluminium round tube, diameter 40 mm and associated aluminium system connectors. The modular and fixed railing system is demountable, changeable and expandable. |  | rm | 0
|  | floor cut-outs | Factory / on-site execution of floor cut-outs for sockets, ventilation outlets, etc. (delete as appropriate) Exact description: ________________________ |  | pcs. | 0
|  | floor cut-outs | Factory / on-site execution of floor cut-outs for sockets, ventilation outlets, etc. (delete as appropriate) OBO Bettermann use: OBO GES 2 OBO GES 4 OBO GES 6 OBO GES 9 OBO GES R4 OBO GES R7 OBO GES R9 (delete as appropriate) |  | pcs. | 0
|  | protective cover | Provide and install protective cover. Protective cover made of wood-based material for temporary closure of floor openings, up to the time of installation of the insert. Opening for OBO GES R9 Opening for _______________ Opening ________ x _________ mm (delete as appropriate) Disassembly and disposal on site. |  | pcs. | 0
|  | installation of sockets | Supplying and installing sockets, swirl outlets, etc. exact description: _________________ |  | pcs. | 0
|  | extra pedestals | Delivery and installation of additional pedestals under panel cut-outs. |  | pcs. | 0
|  | floor finish | Floor finish for transition to the unfinished floor or stairs. Melamine-coated wood-based panel with aluminium tread angle. Deliver and assemble. Ground level as above. |  | rm | 0
|  | shifting prevention | Sliding protection / bracing for free ending raised floor. Consisting of aluminium angle, perforated steel or tie rods and fastening material. |  | rm | 0
|  | protective cover | Covering the finished raised floor area for protection against other construction works. Execution: - Cardboard box - PE foil carton - PE foil carton backed by anti-tread fleece - Hardboard underlaid with anti-tread material (delete non-applicable variants) Dismantling and disposal takes place on site. |  | m² | 0
|  | adjusting | Adjusting the soil after completing the subsequent movements |  | m² | 0
|  | reserve plates | Spare panels for raised floor acc. pos. xxx, incl. covering and delivery |  | pcs. | 0
|  | reserve pedestals | reserve pedestals for raised floor as in pos. xxx, incl. delivery |  | pcs. | 0
|  | toolbox | Tool box for tools, siphon or claw lifter supply. Without tools and lifters. |  | pcs. | 0
|  | lifting device, plastic | Lifting device with two suction cups, to open the raised floor system. |  | pcs. | 0
|  | lifting device, aluminium | Heavy duty lifting device made of aluminium, with two suction cups, for opening the raised floor system. |  | pcs. | 0
|  | lifting device, aluminium | Lifting tool made of aluminium, with 2 needle claw plates, for opening raised floor systems with textile coverings. |  | pcs. | 0
Hourly wage work
|  | hourly wage work | Hourly wage work, which is carried out at the express arrangement of the construction management.
|  | foreman | foreman |  | h | 0
|  | skilled workers | skilled workers |  | h | 0
|  | helper | helper |  | h | 0
|  | night work bonus | Surcharge for night work arranged by the construction management (between 22:00 and 06:00) |  | h | 0
|  | weekend and holiday bonus | Surcharge for work arranged by the construction management on weekends (from Friday 22:00 to Monday 06:00) and public holidays (from the day before the holiday 22:00 clock to the day after the holiday 06:00 clock). |  | h | 0
|  |  | Total hourly wage work |  | h | 0